ONR Assessment Report Generic Design Assessment of the Holtec SMR-300 – Step 2 Assessment of Safeguards

ONR Assessment Report

Project Name: Generic Design Assessment of the Holtec SMR-300

Report Title: Step 2 Assessment of Safeguards

Authored by: Inspector

Assessment report reference: AR 1317

Project report reference: PR 1804

Report issue: 1

Document ID: ONRW-2126615823-8573

Published: December 2025

© Office for Nuclear Regulation, 2025

For published documents, the electronic copy on the ONR website remains the most current publicly available version and copying or printing renders this document uncontrolled. If you wish to reuse this information visit www.onr.org.uk/copyright for details.

# Executive summary

This report presents the outcomes of my Safeguards assessment of the Holtec SMR-300 as part of Step 2 of the Office for Nuclear Regulation (ONR) generic design assessment. This assessment is based upon the information presented in revision 1 of Holtec’s safety, security and environment case (comprising a preliminary safety report, preliminary environment report, preliminary safeguards report, and generic security report), the design reference point, and supporting documentation.

ONR’s generic design assessment process calls for a stepwise assessment, which increases in detail as the project progresses. The focus of my assessment in this step was towards the fundamental adequacy of the SMR-300 design, the operator’s relevant submissions (referred to by the requesting party as the safeguards case), and the suitability of the methodologies, approaches, codes, standards and philosophies which form the building blocks for the design and generic safety and security cases.

In accordance with my assessment plan, I targeted my assessment at the aspects of the SMR-300 design that are novel, contentious, or where significant safeguards claims are made. My expectations were informed by ONR’s nuclear material accountancy, control, and safeguards assessment principles, technical assessment guides and other guidance which ONR regards as relevant good practice.

I targeted the following aspects in my assessment of the SMR-300 design reference point and Holtec’s safety, security and environment case:

which allow me to form a judgement on the fundamentals of the SMR-300 design and safeguards case in line with the objectives of Step 2

which I judge to be the most safeguards significant in the context of the design and safeguards case

where I consider that justification and scrutiny of the design or safeguards case may be needed due to factors such as novelty or uncertainty

where the SMR-300 design or safeguards case differs from established relevant good practice

where I consider there to be a significant risk that the fundamental aspect being assessed will not be able to be substantiated or will not meet regulatory expectations in future project stages

where I consider that attention is needed on a fundamental aspect of the design or safeguards case that may prevent construction and operation of the SMR-300 in Great Britain. These are based upon ONR’s previous experience of generic design assessments (including the generic design assessment technical guidance and my current understanding of the Holtec SMR-300 design)

Based upon my assessment, I have concluded the following:

the requesting party has demonstrated in the preliminary safeguards report an understanding of both domestic and international regulatory requirements and expectations for safeguards commensurate with the current status of the design, including submission of an Article 2.a.(ix) declaration under the UK additional protocol

- the information that has been submitted to demonstrate an understanding of safeguards by design is consistent with ONR’s expectations for the current status of the design

- I am content that sufficient information was provided during Step 2, but further details will be required, for example, on the nuclear material accountancy and control system, and the basic technical characteristics will need to be updated as the design matures

Overall, based on my step 2 assessment, I have not identified any fundamental shortfalls from a safeguards perspective that would prevent ONR permissioning the construction of a power station based on the generic Holtec SMR-300 design.

# List of abbreviations

ALARP	As low as is reasonably practicable

AR		Annular Reservoir

BTC		Basic Technical Characteristics

CES		Containment Enclosure Structure

CS		Containment Structure

DRP		Design Reference Point

FSE		Fundamental Safeguards Expectation

GDA		Generic Design Assessment

GSR		Generic Security Report

IAEA		International Atomic Energy Agency

INFCIRC	IAEA Information Circular

ISFSI		Interim Spent Fuel Storage Installation

MWe		Mega Watts Electrical

NRW		Natural Resources Wales

NSR19	Nuclear Safeguards (EU Exit) Regulations 2019

NMAC	S	Nuclear Material Accountancy, Control and Safeguards

ONMACS 	ONR Guidance on Nuclear Material Accountancy, Control, and Safeguards

ONR		Office for Nuclear Regulation

PSR		Preliminary Safety Report

PSgR		Preliminary Safeguards Report

PWR		Pressurised Water Reactor

QNF		Qualifying Nuclear Facility

QNM		Qualifying Nuclear Material

RCP		Reactor Coolant Pumps

RITE		Risk Informed and Targeted Engagements

RGP		Relevant Good Practice

RP		Requesting Party (Holtec International)

SFP		Spent Fuel Pool

SgC		Safeguards Claim

SgDP		Safeguards Design Principle

SMR		Small Modular Reactor

SRA		State Regulatory Authority

SSAC		State System of Accounting for and Control of Nuclear Material

SSEC		Safety, Security (and Safeguards), Environmental Case.

TAG		Technical Assessment Guide(s) (ONR)

UKAP		UK/IAEA Additional Protocol (INFCIRC/951 Add. 1)

UKVOA	UK Voluntary Safeguards Agreement with the IAEA (INFCIRC/951)

Contents

Executive summary	3

List of abbreviations	5

1.	Introduction	7

2.	Assessment standards and interfaces	9

3.	Requesting party’s submissions	13

4.	ONR assessment	16

5.	Conclusions	24

6.	References	26

Appendix 1 – Relevant ONMACs FSEs considered during the assessment	29

# Introduction

This report presents the outcomes of my Safeguards’ assessment of the Holtec Small Modular Reactor (SMR-300) as part of Step 2 of the Office for Nuclear Regulation (ONR) Generic Design Assessment (GDA). This assessment is based upon the information presented in version 1 of the Holtec SMR-300 Safety, Security, Safeguards, and Environment Case (SSEC) (ref [1]) and (refs. [2], [3], [4], [5], and [6]), the Design Reference Point (DRP) (ref. [7]), Master Document Submission List (MDSL) (ref. [8]) and supporting documentation.

Assessment was undertaken in accordance with the requirements of ONR’s management system. It follows ONR’s Guidance on Production of Reports for Permissioning (ref. [9]) and Risk Informed and Targeted Engagements policy (RITE) (ref [10]), guidance on the Mechanics of Assessment (ref. [11]), ONR Guidance on Nuclear Material Accountancy, Control, and Safeguards  (ONMACS) (ref. [12]), together with the principles detailed in the supporting Technical Assessment Guides (TAGs) (ref. [13]), have been used as the basis for this assessment.

This is a major report (as per ONR’s guidance, NS-TAST-GD-108 (ref. [9]).

## Background

ONR’s GDA process (ref. [14]) calls for a stepwise assessment of the Requesting Party's (RP) submissions with the assessments increasing in detail as the project progresses. Holtec International is the RP for the GDA of the Holtec SMR-300 design. Holtec International has designated Holtec Britain to manage the GDA project, including developing the SSEC. Holtec Britain is a wholly owned UK subsidiary of Holtec International.

In October 2023 ONR, together with the Environment Agency and Natural Resources Wales (NRW), began Step 1 of the GDA for the Holtec SMR-300. Step 1, which is the preparatory part of the design assessment process and mainly associated with initiation of the project and preparation for technical assessment in later steps, was successfully completed in August 2024 (ref. [15]).

Holtec International confirmed that it only intends to complete GDA up to the end of Step 2. The output of a Step 2 GDA is a GDA Statement.

Step 2 commenced in August 2024. The focus of ONR’s assessments in this step is towards the fundamental adequacy of the design and SSEC, and the suitability of the methodologies, approaches, codes, standards and philosophies which form the building blocks for the design and generic SSEC. The objective is to undertake an assessment of the design against regulatory expectations to identify any fundamental safety, security, or safeguards shortfalls that could prevent ONR granting permission for construction of a power station based on the design (ref. [14]).

Prior to the start of Step 2 I prepared a detailed assessment plan for safeguards (ref. [16]). This has formed the basis of this assessment and was also shared with the RP to maximise openness and transparency.

This report describes one of a series of assessments which support ONR’s overall judgements at the end of Step 2 which are recorded in the Step 2 Summary Report (ref. [17]).

## Scope

The assessment documented in this report is based upon the DRP and SSEC for the Holtec SMR-300 as summarised in the SSEC chapters and supporting documentation.

The overall scope of the Holtec SMR-300 GDA is described in (ref. [18]). The GDA scope was agreed in Step 1 although this has been modified, with agreement of the regulators, during Step 2. The RP has indicated that it intends to complete a two step GDA with the objective of receiving a GDA Statement from ONR and has aligned its GDA scope with this objective. The GDA scope defines the generic plant and layout and includes all systems, structures and components that are identified as being important to safety, security and safeguards, all modes of operation, and all stages of the plant lifecycle.

The regulatory delivery strategy for the GDA of the Holtec SMR-300 Step 2 (ref. [19]) sets out the key regulatory objectives to be delivered during this two step GDA, the approach to deliver these, and the assurance and governance activities implemented to track delivery progress, ensure consistency, and accept delivery of the objectives. My safeguards assessment scope is defined in my assessment plan (ref. [16]) which is discussed in detail in sub-section 4.1 and includes the following:

The RPs understanding of the safeguards domestic regulatory requirements under the Nuclear Safeguards (EU Exit) Regulations 2019 (NSR19) (ref. [20]) including the demonstration that they have a good understanding of the nuclear material accountancy of the Qualifying Nuclear Material (QNM) to be used and stored in the reactor, the locations where QNM will be held, the key measurement points (KMPs) and how the QNM will be accounted for, controlled and reported

The RPs understanding of the UK’s international safeguards obligations under the UK/IAEA Voluntary Offer Agreement (UKVOA (ref. [21]) and the potential safeguards measures which may be applied by the IAEA, if the IAEA select the SMR-300 for implementation of safeguards’ verification, as part of any future post Step 2 engagement. If selected, ONR will facilitate interactions with the IAEA to understand the safeguardability of the design and whether the IAEA would wish to implement safeguards measures (ref. [22]). ONR can consider safeguards measures, but it is for the IAEA to make that assessment. These safeguards measures may include containment and surveillance such as seals, cameras, radiation detectors and remote data transmission. The RP should have considered misuse/diversion scenarios and the safeguards measures which could be applied. The RP should also be able to describe access to the core and fuel pool to enable the IAEA to physically verify the inventory if required. The RP should consider how IAEA safeguards measures would be applied in States with Comprehensive Safeguards Agreements, and Euratom safeguards measures if the intent is to build in the EU, as discussed further in paragraph 32 below.

The RPs understanding/approach to safeguards by design and the RPs approach to integrating safeguards into the SSEC case (alongside safety and security)

The RP’s understanding of the requirements of the UK/IAEA Additional Protocol (UKAP) (ref. [23]) to declare nuclear fuel cycle related research and development and/or generic plans for the next ten years relevant to the development of the UK’s civil nuclear fuel cycle

As the regulatory requirements of NSR19 (ref. [20]) are on the operator/licensee of the reactor the RP should be able to demonstrate that they have identified the commitments and assumptions on the future operator and how these will be communicated to the future operator. The RP should also consider future obligations under the UKs Nuclear Cooperation Agreements

Experience from other GDAs, for example the ongoing GE Hitachi GDA, Hinkley Point C and Sizewell C. The safeguards section in the GD-007 technical guidance (ref. [24]) has also been used, albeit noting that the safeguards section requires updating to reflect ONR safeguards status since January 2021 as the UK State System of Accounting for, and Control of, Nuclear Material (SSAC)/State Regulatory Authority (SRA)

# Assessment standards and interfaces

For ONR, the primary goal of the GDA Step 2 assessment is to reach an independent and informed judgment on the adequacy of the design as detailed in the DRP, and the safety, security and safeguards case for the reactor technology being assessed.

ONR has a range of internal guidance to enable inspectors to undertake a proportionate and consistent assessment of such cases. This section identifies the standards which have been considered in this assessment.

This section also identifies the key interfaces with other technical topic areas.

## Standards

- The ONR ONMACS (ref. [12]) constitute the regulatory principles against which the RP’s case is judged. Consequently, the ONMACs are the basis for ONR’s assessment and have therefore been used for the Step 2 assessment of the Holtec SMR-300. The purpose of the ONR ONMACS is to provide safeguards inspectors with a framework for making consistent and proportionate regulatory judgements on the adequacy of an operator’s compliance with NSR19. The ONMACS sets out ONRs regulatory expectations for compliance with NSR19.

The International Atomic Energy Agency (IAEA) safety standards (ref. [25]) are a cornerstone of the global nuclear safety and security regime. They provide a framework of fundamental principles, requirements and guidance. They are applicable, as relevant, throughout the entire lifetime of facilities and activities. The IAEA has published the report ‘Applicability of IAEA Safety Standards to Non-water cooled Reactors and Small Modular Reactors’ (ref. [26]), which, although safety-focussed, identifies specific considerations related to the interfaces between safety, security and safeguards. Examples of safeguards coverage in other IAEA safety standards include: SRR-2/1 (revision 1) Interfaces of safety with security and safeguards; and NNS No.25-G Use of nuclear material accounting and control for nuclear security purposes at nuclear facilities.

- The relevant IAEA standards are embodied and expanded on in the TAGs (ref. [13]).

    - Nuclear Material Accountancy, Control, and Safeguards Assessment Principles (ONMACS) (ref. [12])

- The key ONMACS Fundamental Safeguards Expectations (FSE) applied within my assessment are FSE 5, 6, 7 and 8.

- A list of the ONMACS FSE used in this assessment is recorded in Appendix 1.

### Technical Assessment Guides (TAGs)

- The following TAGs have been used as part of this assessment:

- NS-TAST-GD-096 - Guidance on Mechanics of Assessment (ref. [11])

- ONR, SG-TAST-GD-001 Issue 4 ONR Technical Assessment Guide Safeguards (January 2023) (ref. [27]). This TAG contains guidance to advise and inform ONR safeguards inspectors in the exercise of their regulatory judgement during general assessment activities

- ONR, SG-TAST-GD-002 Issue 3 ONR Technical Assessment Guide Nuclear Material Accountancy (February 2025) (ref. [28]). This TAG contains guidance to advise and inform the ONR inspectors in the exercise of their regulatory judgement during assessment activities relating to data contained within operator inventory change reports (ICRs), material balance reports (MBRs), physical inventory listing (PILs) and special reports required by Regulations 14, 15 and 16 of NSR19

### National and international standards and guidance

- The following international standards and guidance have been used as part of this assessment:

IAEA, Format and Content of the Safety Analysis Report for Nuclear Power Plants, Specific Safety Guide No. SSG-61 (September 2021) (ref. [29])

ONR, SG-INSP-GD-001 ONR Technical Inspection Guide (TIG) Safeguards Issue 4 (January 2023) (ref. [30]). To support inspectors undertaking compliance inspection, ONR produces a suite of guides to assist inspectors to make regulatory judgements and decisions in relation to the adequacy of compliance on the site. This technical inspection guide (TIG) is part of the suite of documents provided by ONR for this purpose

- ONR, CNSS-SAF-GD-001 Guidelines for the preparation and submission of declarations pursuant to Article 2 of the additional protocol to the UK/IAEA safeguards agreement (INFCIRC/951 Add.1), Issue 2 (January 2025) (ref. [31]). The purpose of these guidelines is to assist operators with the provision of information to the ONR as required under INFCIRC/951 Add. 1, the protocol additional to the United Kingdom (UK)/International Atomic Energy Agency (IAEA) safeguards agreement, INFCIRC/951 (ref. [21]).

- IAEA, IAEA NP-T-2.9 International Safeguards in the Design of Nuclear Reactors, STI/PUB/1669 (iaea.org) (ref. [22]). This publication is the second in the IAEA Nuclear Energy Series to provide guidance on the inclusion of safeguards in nuclear facility design and construction, in this case the design of nuclear reactors

- IAEA, International Safeguards in Nuclear Facility Design and Construction, IAEA Nuclear Energy Series No. NP-T-2.8, 2013 (ref. [32]). This IAEA publication provides guidance on the inclusion of safeguards considerations in nuclear facility design and construction. This first volume introduces the basic principles of safeguards by design and discusses the goals, costs and rewards, and places the information into the context of nuclear facility design and construction

- IAEA, Applicability of IAEA Safety Standards to Non-water cooled Reactors and Small Modular Reactors (ref. [26]). The objective of this publication is to present a high level review of the applicability of IAEA safety standards to evolutionary and innovative designs (including SMRs) - in particular, to consider whether the current requirements and recommendations are applicable to these technologies and to identify any gaps. The publication also identifies specific considerations related to the interfaces between safety, security and safeguards.

## Integration with other assessment topics

- I have worked with other topics as part of my safeguards assessment. Similarly, other assessors sought input from my assessment. These interactions are key to the success of GDA to prevent or mitigate any gaps, duplications or inconsistencies in ONR’s assessment.

- The key interactions with other topic areas were:

Fuel cycle/Nuclear Liabilities – Qualifying Nuclear Facilities (QNF) will continue to have safeguards obligations throughout all stages of the nuclear fuel cycle (including decommissioning, long-term storage and disposal on both fuel and other QNM that will not be considered as waste for safeguards’ purposes under NSR19)

Layout – both ONR and IAEA safeguards have the right to install safeguards related equipment (such as cameras, radiation monitors, seals and remote data transmission equipment). Incorporating this potential for installing such equipment, which would be more likely if the facility will be under IAEA safeguards, into the early stages of the project cycle is considered beneficial by all stakeholders, particularly in novel designs having a compact layout as is the case for the SMR-300

Radioactive Waste Management – certain categories of QNM will not be considered as waste therefore safeguards should be included in topics such as long term storage of spent fuel and disposability assessments

Metrication – use of SI units are defined in the legislation and guidance for safeguards reporting

## Use of technical support contractors

During Step 2 I have not engaged technical support contractors to support my safeguards assessment for the Holtec SMR-300.

# Requesting party’s submissions

The RP’s principal submissions are a series of drawings and documents that make up the DRP and a series of SSEC chapters and other supporting references, which provides its preliminary safety, security, safeguards and environment cases for the generic SMR-300 design. This section presents a summary of the SMR-300 design and the RP’s safeguards case. It also identifies the supporting documents submitted by the RP which have formed the basis of my safeguards assessment of the SMR-300.

## Summary of the Holtec SMR-300 design

The Holtec SMR-300 design is a Pressurised Water Reactor (PWR) with a single steam generator, including an integrated pressuriser and two Reactor Coolant Pumps (RCPs) providing forced circulation in normal operation. The electrical power output capacity to the grid is 320 MWe (net) (from a thermal power of 1,050 MWth) with a design life of 80 years for non-replaceable components. The SMR-300 design submitted for assessment in GDA is a twin-unit design comprising two SMR-300 reactors and associated plant.

The SMR-300 is equipped with a number of supporting systems for normal operations and a range of safety measures to provide cooling, criticality control, and contain radioactivity under fault conditions. Passive safety features are preferred to active components, reflecting the RP’s design philosophy.

The SMR-300 has a compact layout. The Reactor Pressure Vessel (RPV), which holds the fuel assemblies, the steam generator, RCPs and associated pipework, the Spent Fuel Pool (SFP) and the passive safety systems, are all held within a steel Containment Structure (CS) and a secondary steel and concrete Containment Enclosure Structure (CES). An Annular Reservoir (AR), containing a large volume of water, is located between the CS and CES. The AR is used to provide the ultimate heat sink to the passive safety systems.

The twin unit design is comprised of two separate reactors in separate containment buildings. Each reactor has dedicated normal operation systems, safety measures and SFP, however there is a single control room for the twin unit SMR-300.

The RP developed the Holtec SMR-300 design based upon well-established PWR technology. The RP claims that the design of the SMR-300 is based upon the following principles:

redundant and passive engineered safety features

simplified plant design with structures designed to withstand all postulated external events

ability to mitigate design basis accidents with no operator action

ability to cope with an extended loss of all AC power for at least 72 hours

defence-in-depth approach to beyond design basis accident mitigation

reliable active systems to support normal plant operation

The SMR-300 layout, in particular the compact size, may have an impact of the ‘safeguardability’ of the reactor (ref. [22]), for example if the reactor is designated for IAEA inspection/verification in the UK (or is considered for construction in other States subject to IAEA safeguards (and Euratom safeguards if an EU State)), this may lead to installation of safeguards-related equipment such as cameras and remote data transmission equipment. The compact size may also impact inspector access when conducting on-site verifications. Safeguardability refers to the extent to which the design of the facility readily accommodates, and facilitates, effective and cost-efficient safeguards.

## SSEC approach and structure

The SSEC for the SMR-300 consists of the PSR, the PER, the Generic Security Report (GSR) (ref. [33]) and the Preliminary Safeguards Report (PSgR), along with their supporting documents. The complete set of SSEC documentation submitted for the GDA is captured within the Master Document Submission List (MDSL) (ref. [8]).

The SSEC has been developed for a twin-unit reactor design to be constructed, operated, and decommissioned on any generic site that is within the bounds of the generic SMR-300 Generic Site Envelope (GSE).

The fundamental purpose of the SSEC is to demonstrate that the SMR-300 can be constructed, commissioned, operated, and decommissioned on a generic site in the United Kingdom (UK) to fulfil the future licensee’s legal duties to be safe, secure and protect people and the environment (ref. [2]).

The SSEC and supporting documents have been prepared using the Claims, Arguments, Evidence (CAE) concept. SSEC Chapter A3 (ref. [34]) provides a high-level route map which links the claims made throughout the SSEC to the fundamental purposes.

## Summary of the requesting party’s case for Safeguards

The RP has stated that the overall aim of the Step 2 is to demonstrate that there are no fundamental safeguards shortfalls that could prevent granting permission for the construction of a power station based on the generic SMR-300 design information, provided for GDA.

The RP has chosen to develop its cases in a holistic manner, as an SSEC. The SSEC is being developed using a three-tier hierarchy and incorporating a CAE structure.

The Preliminary Safeguards Report (PSgR) (ref. [35]) details the RP’s key claims on how it will comply with NSR19 and support UK delivery of its international obligations. The key claims made are:

### Safeguards Claim SgC 1

- Undeclared withdrawal of a Significant Quantity of Qualifying Nuclear Material from the generic SMR-300 will be detected in a timely manner in accordance with the UKVOA.

### Safeguards Claim SgC 2

- The generic Holtec SMR-300 designer/operator will provide the reporting required under the AP.

### Safeguards Claim SgC 3

The generic Holtec SMR-300 designer/operator will support ONR in its enforcement of NSR19

## Demonstrating Risks are Reduced by Safeguards By Design

The RP states that safeguards by design is being implemented in the evolving generic SMR-300, and that safeguards are informing the design and layout. Holtec recognises that a robust safeguards management system and culture are required at all stages of the SMR-300 project lifecycle to ensure it can demonstrate that the UK safeguards regulatory framework and expectations are being accommodated, for example in sub-sections 5.9.3.and 5.9.3.1 of Chapter A 5 ALARP (ref. [36]) and Revision 2 of the PSgR (ref. [35]).

## Basis of assessment: requesting party’s documentation

The principal documents that have formed the basis of my Safeguards assessment are:

- Holtec SMR-300 Safeguards by Design Basic Technical Characteristics HI-2241030 Revision 2 (25 April 2025) (ref. [37])

This document details information including the description of the current facility design along with the expected form, quantity, location and flow of QNM. This document enables ONR to understand the safeguards-relevant characteristics of the facility design and to assess if the RP has adequately considered ONR and international safeguards expectations. The IAEA can use the BTC to help design a facility safeguards approach if IAEA safeguards measures are to be applied to the facility.

- Holtec, SMR-300 Preliminary Safeguards Report HI-2240260 Revision 2 (27 May 2025) (ref. [35])

This document is used to demonstrate the RP’s understanding of both the UK and international safeguards expectations. The RP also uses it to demonstrate that the SMR-300 design can facilitate these expectations.

- Holtec International, SMR-160 Design Standards for Security and Safeguards’ Report No. HPP-160-3012, Revision 0 (24 July 2024) (ref. [6]).

The RP states that the purpose of the Design Standard is to describe the United States Nuclear Regulatory Commission (USNRC), Canadian Nuclear Safety Commission (CNSC), and the International Atomic Energy Agency (IAEA) security and safeguards regulatory requirements applied to the SMR-160 nuclear power plant to provide guidance to designers on how to consider these requirements in the design phase in an integrated manner.

- Holtec SMR GDA PSR PART A Chapter 5 Summary of ALARP HI-2240336 Revision 1 (4 July 2025) (ref. [36]).

The RP states that the purpose of this Chapter is to summarise the PSR and conclude whether the PSR Fundamental Objective has been met and that the risks associated with the SMR-300 are likely to be tolerable and ALARP. Further, it aims to draw together the outcomes of the PER, GSR and PSgR against their objectives to demonstrate that the Fundamental Purpose of the SSEC has been met.

# ONR assessment

## Assessment strategy

In line with the objectives for a two step GDA, I undertook a high-level review of the RPs SSEC and DRP to identify any key claims made on safeguards or areas where safeguards considerations may affect the design and is detailed in sub-section 4.2.

## Assessment

Safeguards By Design (SBD) (refs [22], [32] and [26]) is defined as “the provision of guidance to State authorities, designers, equipment providers and prospective purchasers on the importance of taking international safeguards into account when designing a nuclear facility or process”. A voluntary best practice, SBD allows for informed design choices that optimise economic, operational, safety and security factors, in addition to international safeguards. It is applicable to all stages of the nuclear fuel cycle, from initial planning and design through construction, operation, waste management and decommissioning. For new nuclear facilities, especially novel designs or processes, the earlier the discussion of safeguards the better: SBD allows for safeguards to be built ‘into’ the system, rather than around it afterwards.

The IAEA’s SBD guidance documents informing this assessment were:

IAEA NP-T-2.9 International Safeguards in the Design of Nuclear Reactors STI/PUB/1669 (iaea.org) (ref. [22])

International Atomic Energy Agency, International Safeguards in Nuclear Facility Design and Construction IAEA Nuclear Energy Series No. NP-T-2.8 (2013) (ref. [32])

Applicability of IAEA Safety Standards to Non-water-cooled Reactors and Small Modular Reactors Safety Report Series Number 123 (2023) (ref. [26])

ONR’s guidance: New Nuclear Power Plants: Generic Design Assessment Guidance to Requesting Parties, ONR-GDA-GD-006 (ref. [14]) contains few references to safeguards. More detailed guidance on safeguards’ expectations can be found in New Nuclear Power Plants: Generic Design Assessment Technical Guidance ONR-GDA-GD-007 Revision 0 (May 2019) (ref. [24]). The latter requires updating to reflect the UK’s role as the State Regulatory Authority responsible for the State System of Accountancy and Control since 31 December 2020 following commencement of regulation under NSR19. Chapter 3 of this technical guidance for GDA provides guidance to RPs on ONR’s expectations, with safeguards expectations set out in sub-section 3.17.

The following assessment is informed by the expectations in GD-007. The main areas of safeguards interest for new types of nuclear facility are for the RP’s to:

- Define and agree nuclear materials accountancy, control and safeguards (NMAC&S) arrangements for the facility design, including the process and timeline for specifying and installing any surveillance, monitoring and other safeguards equipment that may be required as part of verification by the IAEA

- Ensure all statutory safeguards reporting requirements (e.g. for reporting as set out in the safeguards regulations and consideration of the UK’s Nuclear Cooperation Agreements requirements) are met

I have reviewed the RPs approach in developing its safeguards case as part of a holistic SSEC. This approach is relatively novel. The existing nuclear facilities in the UK were constructed prior to NSR19 coming into force in 2021. Holtec has, therefore, had the benefit of being able to create integrated safety, security, and environment cases (including safeguards) which existing facilities were unable to do. The integrated approach should lead to better clarity of systems which are important to all areas and enable for simplification of documentation and operational requirements. I judge that the claims used, together with sub-section 4.2.4, cover safeguards expectations.

### Safeguards Claim SgC 1 - Undeclared withdrawal of a Significant Quantity of Qualifying Nuclear Material from the generic SMR-300 will be detected in a timely manner in accordance with the UKVOA.

Following the UK departure from the EU, the UK and IAEA agreed a bilateral Voluntary Offer Safeguards Agreement (UKVOA, INFCIRC/951 which came into force on 12 January 2021) (ref. [21]). This replaced the previous trilateral safeguards agreement that also included Euratom. The objective of the UKVOA is set out in Article 27: “The objective of the safeguards procedures set forth in this part of the Agreement is the timely detection of withdrawal from civil activities, except as provided for in this Agreement, of significant quantities of nuclear material which is being safeguarded in facilities or parts thereof designated pursuant to Article 76(a)”.

The RP has claimed in SgC1 that the undeclared withdrawal of a significant quantity of QNM from the generic SMR-300 will be detected in a timely manner in accordance with the UKVOA. Safeguards claim SgC1 is further sub-divided into three sub-claims, which cover the areas of (i) inherent proliferation resistance; (ii) implementation of a robust NMAC system; and (iii) inspection and independent verification. Proliferation resistance was not included in the safeguards assessment as proliferation resistance is not a safeguard but includes safeguards as a key component. Proliferation resistance is a broader characteristic of a nuclear energy system that impedes the diversion of materials or technology for nuclear weapons. Proliferation resistance is achieved through a combination of intrinsic (technical design) and extrinsic measures, which include international safeguards. Safeguards are the "extrinsic" measures that verify that countries are complying with their nuclear non-proliferation obligations.

The RP has discussed misuse of the facility in PSgR sub-sections 5.2.2 and 7.2.1. Misuse can be considered as ‘misuse of a safeguarded facility for undeclared activities or the undeclared production of weapons usable material.’ The RP states in sub-section 5.2.2 of the PSgR that one activity during design development would be to “Build inherent proliferation resistance in the design of the SMR-300 by, for example by minimising the possibility of misuse of the plant”. Subsection 7.2.1 states that consideration during design will be given to optimisation of layout/space to prohibit the covert misuse of the SMR-300 site for proliferation purposes. I judge that the RP has addressed the need to consider misuse in the design of the SMR-300.

In the PSgR (ref. [35]) the RP demonstrates its understanding of the UK’s obligations under the non-proliferation treaty through the UKVOA and how these flow into the requirements placed on it as designer under NSR19 and ONR’s guidance (ONMACS). I have reviewed the PSgR, and I judge that the RP has clearly and accurately understood the regulatory requirements and expectations for safeguards in the UK.

The RP also claims that it understands the safeguards requirements for operating a reactor in the UK. I have reviewed the PSgR (ref. [35])  and judge that it demonstrates a clear and accurate understanding of the UKs obligations and how these flow down through NSR19 and regulatory guidance (ONMACS) into requirements for constructing and operating the SMR-300. PSgR sub-section 3.0 describes in detail the UK’s international and national agreements and obligations: Nuclear Non-Proliferation Treaty; the UK Voluntary Offer Agreement; and the UK Additional Protocol (sub-section 3.1 International Framework). The RP also demonstrates an understanding that, in the UK, parts of NSR19 are prescriptive and enable the UK to fulfil its international safeguards’ obligations.

I judge that the information that has been submitted to demonstrate an understanding of international safeguards obligations in our UKVOA and UKAP is consistent with ONR’s expectations for the current status of the design and should enable the RP to further develop the generic SMR-300 design and associated safeguards case evidence. I judge that, based on the sampled evidence assessed in this section, I have not identified any fundamental safeguards shortfalls that could prevent ONR permissioning the construction of a power station based on the generic SMR-300 design. The PSgR has a high-level reference to the UK’s Nuclear Cooperation Agreements (NCAs). These could place additional reporting and oversight burdens on the operator, but I judge this is not a fundamental shortfall.

### Safeguards Claim SgC 2 The generic Holtec SMR-300 designer/operator will provide the reporting required under the AP

PSgR sub-section 3.2 and sub-section 7.3 (Safeguards Claim 2 – UKAP reporting) describes the requirements of the UKAP, noting that the RP has been submitting an Article 2.a.(ix) declaration (Ten Year Plans for development of the UK nuclear fuel cycle) as contribution to the annual UK calendar year Article 2 update for at least two years; ONR has reviewed their submissions and judged that they contain the information required to be included in that calendar year’s update (refs. [23] and [31]).

### Safeguards Claim SgC 3 The generic Holtec SMR-300 designer/operator will support ONR in its enforcement of NSR19

Chapter 3.0 of the PSgR covers the international and national safeguards framework. Sub-section 3.3 discusses the UK safeguards legal basis and regulatory framework. I judge that the RP has correctly identified the basis for the delivery of UK’s safeguards obligations including NSR19 as being made to define the domestic safeguards regime and the establishment of ONR as the UK safeguards regulator. I judge that the RP has also correctly identified the role of ONR as the State Regulatory Authority responsible for establishing, implementing and maintaining the UK State System of Accountancy for, and Control of, nuclear material (SSAC) is also discussed.

The PSgR also covers a number of other related NSR19 safeguards expectations/requirements including international and national safeguards guidance; an overview of the safeguards programme; design considerations in support of NMAC, including a proposed MBA/KMP structure; and safeguards expectations (FSEs and MACEs). I judge that the RP has correctly identified a possible MBA/KMP structure for a two-unit reactor facility with a number of shared support structures. I also judge that this possible MBA/KMP structure would allow the UK to meet its relevant international safeguards obligations.

Sub-section 2.7.3. of the PSR Chapter 2 (General Design Aspects and Site Characteristics) discusses the international and UK safeguards framework. The RP claims in Segment A2 that the Preliminary Safeguards Report demonstrates Holtec’s understanding of safeguards requirements at the generic (international and UK) level and how they are being accommodated in the generic design of the SMR-300. I judge that the objectives presented in Chapter A2 are sufficient to meet ONR’s safeguards expectations. The RP has covered relevant aspects such as presenting their understanding of the safeguards requirement at the generic (international and UK domestic) level and of relevant good practice. The RP has also discussed the accommodation of safeguards requirements in the generic SMR-300 design, including information on the development of the safeguards design objectives, safeguards design principles, and the implementation of safeguards by design. The RP has also covered potential future requirements, for example outlining the evolution from GDA Step 2 to site licensing in the safeguards area, in accordance with the SMR-300 safeguards programme.

The RP has submitted a UK GDA SMR-300 SSEC Structure (ref [1]). I judge that the RP has recognised the requirement to demonstrate that they have identified the commitments and assumptions on the future operator and how these will be communicated to the future operator. Sub-section 4.4 of the RP’s GDA SSEC states that they will outline the SMR-300 safeguards programme on how the safeguards requirements will be delivered for the SMR-300 through all phases of its lifecycle and its implementation during the GDA. Sub-section 4.4 also outlines the evolution from GDA Step 2 to site licensing in the safeguards area, in accordance with the SMR-300 safeguards programme.

In support of the RP’s claim to recognise the requirement to identify future commitments and assumptions on the future operator and how these will be communicated to the future operator, sub-section 5.2.3 of the PSgR (Site-Specific Design to Start of Operations) describes  the activities to be undertaken during this early stage of the project up to the transition from the RP to the site-specific SMR- 300 operator. Further information, sub-section 5.2.4 identifies the activities in the SMR-300 safeguards programme from the operational phase through to decommissioning. Future inspection and verification activities are covered in several areas in the PSgR with the main consideration of these in future activities found in sub-section 7.2.3 SgC 1.3 (Inspection and Independent Verification). The RP’s Safeguards Design Principle (SgDP) correctly identifies that independent verification and inspection by ONR/IAEA shall be facilitated by the operator. SgDP 3.1 correctly identifies that the SMR-300 plant layout shall provide the necessary services (e.g. uninterruptible power supply) to operate and maintain any safeguards equipment used for independent verification. I judge that the RP has correctly identified a range of future commitments and assumptions and how these will be communicated to a future operator/licensee.

I judge that, in the PSgR (ref. [35]), the RP demonstrates their understanding of the UKs obligations under the non-proliferation treaty through the UKVOA and UKAP and how these flow into the requirements placed on it as designer under NSR19 and ONRs guidance (ONMACS). I have reviewed the PSgR, and I judge that the RP has clearly and accurately understood the regulatory requirements and expectations for safeguards in the UK.

NSR19 places a number of duties on dutyholders/licensees including establishing, implementing and maintaining a system of accountancy and control of QNM in each QNF. Noting that at present there is no licensee or operator, the RP has captured the following high-level commitments for any future licensee:

Sub-section 4.4 of the RP’s GDA SSEC states that they will outline the SMR-300 safeguards programme on how the safeguards requirements will be delivered for the SMR-300 through all phases of its lifecycle and its implementation during the GDA and outlines the evolution from GDA Step 2 to site licensing in the safeguards area, in accordance with the SMR-300 safeguards programme

Attachment 28.1 of the BTC recognises that the future efficacy of the NMAC system can be influenced by defining Material Balance Areas (MBA) where flows and inventory of QNM can be determined, establishing Key Measurement Points (KMP) within those MBA where flows and inventories of nuclear material can be measured and recognising existing, and the potential for new, reporting requirements and obligations. This will provide a foundation for development in the future as the design matures

I judge that, in paragraph 60 above, the RP has correctly identified those  commitments for any future dutyholder/licensee. I have assessed the RP’s proposed NMAC system to account for and control QNM and the reporting structure for submitting the required NSR19 safeguards report. I judge that these are adequate for a fundamental safeguards assessment and that the RP has demonstrated that the QNM can be monitored and controlled in line with regulatory expectations. The RP has noted that it will continue to develop these arrangements as the detailed design progresses. These will be reviewed in any future regulatory engagements. As the regulatory requirements of NSR19 are on the operator/licensee of the reactor, the RP should be able to demonstrate that they have identified the commitments and assumptions on the future operator and how these will be communicated to the future operator. I judge that the RP has identified these commitments in the SSEC Case structure and sub-section 5.2.3. of the PSgR.

I judge that the information that has been submitted to demonstrate an understanding of future regulatory requirements of NSR19 is consistent with ONRs expectations for the current status of the design and should enable the RP to further develop the generic SMR-300 design and associated safeguards case evidence. I judge that, based on the sample evidence assessed in this section, I have not identified any fundamental safeguards shortfalls that could prevent ONR permissioning the construction of a power station based on the generic SMR-300 design.

### Demonstrating Risks are Reduced by Safeguards By Design

The RP claims that the SMR-300 has been designed with safeguards in mind. The SMR-300 was predominantly designed against USNRC expectations; however, the RP states it has also considered UK and IAEA standards in its submissions. I have reviewed the PSgR, BTC, Design Standard for Security and Safeguards and Summary of ALARP. I judge that these are consistent with IAEA guidance NP-T-2.9 International Safeguards in the Design of Reactors, NP-T-2.8 International Safeguards in Nuclear Facility Design and Construction and IAEA Safety Reports Series Number 123; and Applicability of IAEA Safety Standards to Non-Water Cooled Reactors and Small Modular Reactors (refs. [22], [32]), and [26] respectively) and UK expectations detailed in the ONMACS and TAGs. I also judge that the information in the BTC demonstrates the RP has a clear understanding of safeguards by design and the design information required by NSR19. For example, the RP has provided a range of technical information under the various sections of the BTC including plant layout, fuel design and QNM flow from receipt through to shipment out of the MBA. The RP has outlined a potential MBA/KMP structure taking account of a possible two-unit QNF. The RP has claimed that the proposed MBA/KMP structure, as described in the BTC and PSgR, demonstrates an understanding of SBD. I judge that this claim is correct given the current state of the design.

In the PSgR and BTC, I judge that the RP demonstrates an understanding of the fundamental principles for safeguards by design contained in the IAEA guidance for safeguards by design. This includes those contained in (refs. [22], [32]), and [26]).

The RP claims that the information presented in the RP’s Design Standard for Security and Safeguards (ref. [6]) lists examples of the potential safeguards measures that may be applied by the IAEA. The RP claims that the information, originally produced for the SMR-160, is also relevant for the SMR-300 design. I judge that the RP is correct in stating that the information can be used for the SMR-300 design, as these potential safeguards measures could be implemented in the SMR-300.

In the Basic Technical Characteristics (BTC) document I judge that the RP has correctly used Questionnaire 1A Reactors from Part 1, Schedule 1 of NSR19 as required by NSR19 Regulation 3. I judge that the BTC contains  the available safeguards-relevant information given the current status of the SMR-300 design including details at a high technical level on:

Reactor MBA/KMP structure:

The storage areas for incoming QNM

Reactor area for details on refuelling

Storage areas for spent fuel and other non-fuel QNM

Description of and the flow of QNM, including non-fuel QNM

Preliminary MBA structure for the Interim Spent Fuel Storage Installation (ISFSI)

Subsection 8.2.3.of the PSgR describes the Safeguards Design Principles (SgDP) to be incorporated to cover aspects related to the ‘safeguardability’ of the SMR-300. For example, SgDP 2.1 states “ The SMR-300 plant layout shall provide sufficient space to accommodate, operate and maintain the NMAC systems.” BTC attachment 17.1 (Flow of QNM ) describes the flow of QNM through the proposed MBA structure which highlights the possible KMPs at which material can be measured (inventory KMPs) and movements recorded (flow KMPs). I judge that these, in conjunction with the Design Reference Standard for Security and Safeguards which lists some of the possible safeguards equipment that could be installed as part of a safeguards approach, demonstrates the RP’s  understanding of the safeguardability’ of the SMR-300.

I judge that the information that has been submitted to demonstrate an understanding of safeguards by design is consistent with ONR expectations for the current status of the design and should enable the RP to further develop the generic SMR-300 design and associated safeguards case evidence. I judge that, based on the sample of evidence assessed in this section, I have not identified any fundamental safeguards shortfalls that could prevent ONR permissioning the construction of a power station based on the generic SMR-300 design.

# Conclusions

- This report presents the Step 2 safeguards assessment for the GDA of the Holtec SMR-300 design. The focus of my assessment in this step was towards the fundamental adequacy of the design and safeguards case. I have assessed the SSEC, SMR-300 design, and relevant supporting documentation provided by the RP to form my judgements. I targeted my assessment, in accordance with my assessment plan (ref. [16]), at the aspects of the SMR-300 design that are novel, contentious, or where significant safeguards claims are made.  My expectations were informed by ONR’s ONMACS, TAGs and other guidance which ONR regards as relevant good practice.

- Based upon my assessment, I have concluded the following:

the RP has demonstrated in the PSgR understanding of both domestic and international regulatory requirements and expectations for application of safeguards to nuclear material commensurate with the current status of the design, including submission of an Article 2.a.(ix) declaration under the UK additional protocol

- the information that has been submitted to demonstrate an understanding of safeguards by design is consistent with ONRs expectations for the current status of the design

- I am content that sufficient information was provided during step 2, but further details will be required on the NMACS system and the BTC will need to be updated as the design matures beyond this GDA

The information that has been submitted on this topic is consistent with UK and international relevant good practice (ONMACS and IAEA SBD guidance). If the RP continues to develop the SMR-300 design and SSEC on this basis I consider it likely that the final design will be compliant with UK safeguards regulatory requirements and expectations. ONR will assess the final design and SSEC in future activities if the RP continues with its plans to deploy the SMR-300 in the UK.

Overall, based on my assessment to date, and subject to the provision and assessment of suitable and sufficient supporting evidence, I have not identified any fundamental safeguards shortfalls that could prevent ONR granting permission for construction of a power station based on the generic Holtec SMR-300 design.

# References

| [1] | Holtec, Holtec SMR-300 Through-Life Safety, Security and Environmental Case (SSEC) Strategy HI-2241455 Revision 0, 30 January 2025, ONRW-2019369590-16897. |
| --- | --- |
| [2] | Holtec, Holtec SMR GDA PSR PART A Chapter 1 Introduction, Revision 1, 4 July 2025, ONRW-2019369590-22263. |
| [3] | Holtec, Holtec International, SMR-300 GDA PSR PART B Chapter 24 Fuel Transport and Storage HI-2240353 Revision 1, June 2025, ONRW-2019369590-21948. |
| [4] | Holtec, SMR-300 Plant Overview - Non Proprietary Version HI-2240590 Revision 0, 9 May 2024, ONRW-2019369590-9413. |
| [5] | Holtec, Holtec International, SMR-160 Fuel Handling and Storage HI-2188434 Revision 1, 11 July 2025, ONRW-2019369590-22397. |
| [6] | Holtec, Holtec International, SMR-160 Design Standards for Security and Safeguards’ Report No. HPP-160-3012, Revision 0, 24 July 2024, ONRW-2019369590-11409. |
| [7] | Holtec, Holtec International, GDA Design Reference Point HI-2240648 Revision 2.0, 21 May 2025, ONRW-2019369590-20879. |
| [8] | Holtec, Holtec Britain, Master Document Submission List, HI-2240061 Revision 17, 27 November 2025, ONRW-2019369590-25528. |
| [9] | ONR, NS-TAST-GD-108 Guidance on Production of Reports for Permissioning Issue 2, December 2023. |
| [10] | ONR, ONR-RD-POL-002 Risk Informed and Targeted Engagements (RITE) Policy, Issue 2, May 2024. |
| [11] | ONR, NS-TAST-GD-096 Guidance on Mechanics of Assessment Issue 1.2, December 2022. |
| [12] | ONR, ONR-SAF-FW-001 ONR Nuclear Material Accountancy, Control, and Safeguards Assessment Principles (ONMACS) Issue No. 6, February 2025. |
| [13] | ONR, Technical Assessment Guides. //www.onr.org.uk/operational/tech_asst_guides/index.htm. |
| [14] | ONR, ONR-GDA-GD-006 Guidance to Requesting Parties on the Generic Design Assessment (GDA) process for safety and security assessments of new Nuclear Power Plants (NPP) Revision 1, August 2024. |
| [15] | ONR, Holtec SMR-300 Step 1 Statement, August 2024, ONRW-2019369590-11081. |
| [16] | ONR, Step 2 Safeguards Assessment Plan for the Generic Design Assessment of the Holtec SMR-300 Issue 1, 4 September 2024, ONRW-2126615823-3514. |
| [17] | ONR, Generic Design Assessment of the Holtec SMR-300 – Step 2 Summary Issue 1, January 2026, ONRW-2019369590-22557. |
| [18] | Holtec, Holtec Britain, SMR-300 UK Generic Design Assessment Scope HI-2240121 Revision 1, 24 May 2024, ONRW-2019369590-9727. |
| [19] | ONR, Regulatory Delivery Strategy for the Generic Design Assessment of the Holtec SMR-300 Step 2, 3 February 2025, ONRW-2019369590-15040. |
| [20] | ONR, The Nuclear Safeguards (EU Exit) Regulations 2019 No. 196, February 2019. |
| [21] | IAEA INFCIRC/951 Agreement between the UK and the IAEA for the Application of Safeguards in the UK in Connection with the Treaty on the Non-Proliferation of Nuclear Weapons, January 2021. |
| [22] | IAEA, NP-T-2.9 International Safeguards in the Design of Nuclear Reactors, STI/PUB/1669, 2014. |
| [23] | IAEA INFCIRC/951 Add.1 Protocol Additional to the Agreement between the UK and the IAEA for the application of Safeguards in the UK in Connection with the Treaty on the Non-Proliferation of Nuclear Weapons, January 2021. |
| [24] | ONR, ONR-GDA-GD-007, New Nuclear Power Plants: Generic Design Assessment Technical Guidance Revision 0, May 2019. |
| [25] | IAEA, IAEA Safety Standards. www.iaea.org.. |
| [26] | IAEA, Safety Report Series Number 123, Applicability of IAEA Safety Standards to Non-water cooled Reactors and Small Modular Reactors, 2023. |
| [27] | ONR, SG-TAST-GD-001 Issue 4 ONR Technical Assessment Guide Safeguards, January 2023. |
| [28] | ONR, SG-TAST-GD-002 Issue 3 ONR Technical Assessment Guide Nuclear Material Accountancy, February 2025. |
| [29] | IAEA, Specific Safety Guide No. SSG-61, Format and Content of the Safety Analysis Report for Nuclear Power Plants, September 2021. |
| [30] | ONR, SG-INSP-GD-001 Issue 4 ONR Technical Inspection Guide (TIG) Safeguards, January 2023. |
| [31] | ONR, CNSS-SAF-GD-001 Issue 2 Guidelines for the preparation and submission of declarations pursuant to article 2 of the additional protocol to the UK/IAEA safeguards agreement (INFCIRC/951/Add.1), 2 January 2025. |
| [32] | IAEA, International Safeguards in Nuclear Facility Design and Construction IAEA Nuclear Energy Series Number NP-T-2.8, 2013. |
| [33] | Holtec, Holtec SMR-300 Generic Security Report (GSR), HI-2240878, Revision 0, 3 June 2025, ONRW-2019369590-21391. |
| [34] | Holtec, Holtec Britain, PSR PART A Chapter 3 Claims, Arguments and Evidence, HI-2240334, Revision 1, 4 July 2025, ONRW-2019369590-22262. |
| [35] | Holtec, Holtec SMR-300 Preliminary Safeguards Report HI-2240260 Revision 2, 27 May 2025, ONRW-2019369590-21002. |
| [36] | Holtec, Holtec SMR GDA PSR PART A Chapter 5 Summary of ALARP HI-2240336 Revision 1, 4 July 2025, ONRW-2019369590-22265. |
| [37] | Holtec, Holtec SMR-300 Safeguards by Design Basic Technical Characteristics HI-2241030 Revision 2, 25 April 2025, ONRW-2019369590-20151. |

# Appendix 1 – Relevant ONMACs FSEs considered during the assessment

| Fundamental Safeguards Expectation |  |  |
| --- | --- | --- |
| ONMACS No. | SAP Title | Description |  |
| FSE 5 | Reliability, Resilience and Sustainability | The NMACS regime should be designed as such to ensure it is resilient, sustained and remains relevant and proportionate throughout the entire lifecycle of the facility |  |
| FSE 6 | Measurement Programme and Control | Where measurements are designed to be performed, there must be robust systems to ensure the appropriate performance of measurement systems that provide data for the purpose of NMACS |  |
| FSE 7 | Nuclear Material Tracking | The NMACS system should be designed to be able to provide identification, quantity and characteristics to track and QNM in the QNF at any time |  |
| FSE 8 | Data processing and Control | Operators must implement and maintain data processing systems that can produce the NMACS reports, and records required under NSR19 that incorporate technical and procedural controls to protect the confidentiality, integrity, and availability of sensitive nuclear information. |  |