ONR Project Assessment Report Astute Class Submarine Maintenance at Devonport Royal Dockyard – Commencement of Astute Class Submarine Base Maintenance Periods in 15 Dock

ONR Project Assessment Report

Project Name: Astute Class Submarine Maintenance at Devonport Royal Dockyard

Report Title: Commencement of Astute Class Submarine Base Maintenance Periods in 15 Dock

Dutyholder/ Applicant: Devonport Royal Dockyard Ltd.

Report Issue No.: 1

Publication Date:

Document ID: ONRW-2019369590-8249

© Office for Nuclear Regulation, [2025]

For published documents, the electronic copy on the ONR website remains the most current publicly available version and copying or printing renders this document uncontrolled. If you wish to reuse this information visit www.onr.org.uk/copyright for details.

# Executive Summary

Devonport Royal Dockyard Ltd. (DRDL), as the licensee of the Devonport Royal Dockyard nuclear licensed site, has requested the Office for Nuclear Regulation’s (ONR) agreement to undertake the docking and associated Base Maintenance Period upkeep of Astute Class (ABMP) submarines in 15 Dock. This request has been made in accordance with DRDL’s arrangements made under Licence Condition (LC) 22(1): Modification or experiment on existing plant.

DRDL has developed the capability to carry out ABMP in the 15 Dock facility, located within the nuclear licensed site at Devonport Royal Dockyard. This facility is a purpose-built dry dock which has been used for the continual upkeep of nuclear submarines, with the Trafalgar class submarines being the most recent. In preparation for readiness to commence ABMP, 15 Dock has been subject to an extensive outage, which has included maintenance, refurbishment and upgrade works on the facility structures, systems and components. DRDL’s request is supported by a plant safety case to justify the safety of the associated activities.

The recommended regulatory permissioning decision for DRDL to commence its proposed activity has been informed by discipline specific advice from specialist fault studies, human factors, control and instrumentation, mechanical engineering and civil engineering safety inspectors via a combination of targeted assessments and inspections.

All specialist inspectors have advised that there are no safety shortfalls that would prevent ONR agreeing to DRDL’s request. The inspectors did identify some shortfalls against regulatory expectations and have raised associated recommendations. However, all the inspectors judge that they are not prerequisites to ONR’s agreement as they don’t undermine DRDL’s demonstration that risks have been reduced to as low as reasonably practicable (ALARP) and can be addressed as forward action plans.

Based on the work carried out by ONR, I judge that for the requested agreement, DRDL has provided adequate documentation to justify the safety of the proposed modification and demonstrated that there will be suitable and sufficient safety measures in place to ensure that the risks from normal activities and reasonably foreseeable faults will be ALARP. We have not identified any safety shortfalls that would prevent agreement to DRDL’s request and as such, I judge that DRDL has adequately implemented its arrangements made under LC 22(1).

In accordance with the provisions made in DRDL’s arrangements under LC 22(1), I recommend that ONR should issue Licence Instrument 569 agreeing to DRDL’s request for ONR’s agreement to undertake the docking and associated Base Maintenance Period upkeep of Astute Class (ABMP) submarines in 15 Dock. ONR should also maintain regulatory oversight and routinely monitor progress against the identified assessment recommendations via formal regulatory issues to ensure that they are adequately addressed by DRDL within the required timescales

Table 2: List of abbreviations

| Term/Acronym | Description |
| --- | --- |
| ABMP | Astute Base Maintenance Period |
| ALARP | As low as reasonably practicable |
| C&I | Control and instrumentation |
| DRDL | Devonport Royal Dockyard Ltd. |
| DNSR | Defence Nuclear Safety Regulator |
| LC | Licence Condition |
| NSC | Nuclear Safety Committee |
| ONR | Office for Nuclear Regulation |
| PSC | Plant Safety Case |
| RGP | Relevant Good Practice |
| SAP | Safety Assessment Principle(s) |

Table of Contents

Executive Summary	3

1.	Permission Requested	6

2.	Background	6

3.	Assessment and Inspection Work Carried out by ONR in Consideration of this Request	6

4.	Matters Arising from ONR’s Work	7

4.1.	ONR’s Work	7

4.2.	External Governance and Assurance	11

5.	Conclusions	11

6.	Recommendations	11

References	12

# Permission requested

Devonport Royal Dockyard Ltd. (DRDL), as the licensee of the Devonport Royal Dockyard nuclear licensed site, has requested the Office for Nuclear Regulation’s (ONR) agreement to undertake the docking and associated Base Maintenance Period upkeep of Astute Class (ABMP) submarines in 15 Dock [ref. [1]]. This request has been made in accordance with DRDL’s arrangements made under Licence Condition (LC) 22(1): Modification or experiment on existing plant [ref. [2]].

# Background

DRDL has developed the capability to carry out ABMP in the 15 Dock facility, located within the nuclear licensed site at Devonport Royal Dockyard. This facility is a purpose-built dry dock which has been used for the continual upkeep of nuclear submarines, with the Trafalgar class submarines being the most recent.

The facility comprises plant and equipment including dry dock structures, dockside cranes, supporting services (electrical and cooling water systems) and dockside buildings. In preparation for readiness to commence ABMP, 15 Dock has been subject to an extensive outage, which has included maintenance, refurbishment and upgrade works on the facility structures, systems and components. A significant proportion of these works has focussed on the dockside cranes and dock water retaining boundary. The outage has also included implementation of a new Astute class-specific plant safety case (PSC), which includes some revised operator safety actions, operating instructions and associated personnel training to those previously used for Trafalgar class maintenance.

In accordance with its arrangements, DRDL has sought ONR’s agreement to commence ABMP in 15 Dock with the safety of these activities being justified by a supporting PSC [ref. [3]]. This project assessment report provides my recommended decision on DRDL’s request. It is deliberately circumspect in some of the facility and process descriptions and details to be consistent with the document security classification. It has been produced in accordance with ONR’s business management system and associated relevant guidance [ref. [4]].

# Assessment and inspection work carried out by ONR in consideration of this request

Based on the work outlined in Section 2 above and in accordance with the agreed regulatory permissioning strategy for DRDL’s request [ref. [5]] I sought specialist safety inspector advice from the following disciplines to inform the recommended permissioning decision:

Fault studies

Human factors

Control and instrumentation (C&I)

Mechanical engineering

Civil engineering

The recommended permissioning decision for DRDL to commence its proposed activity has been informed by discipline specific advice via a combination of targeted assessments and inspections with the latter focussing on the adequacy of DRDL’s implementation of its arrangements for compliance with LC 22: Modification or experiment on existing plant and LC 28: Examination, inspection, maintenance and testing.

In accordance with the ONR/Environment Agency Memorandum of Understanding (MoU) [ref. [6]], I have consulted with the Environment Agency whether it had any objections, on environmental grounds, to ONR agreeing to DRDL’s request. Similarly, in accordance with the ONR/Ministry of Defence MoU [ref. [6]], I have consulted with the Nuclear Safety Regulator (DNSR) whether it had any objections to ONR agreeing to DRDL’s request from a through-life nuclear safety perspective of the submarine nuclear reactor plant including seeking mutual assurances on relevant safety claims relating to this plant (for which DNSR is the competent body).

To initiate the regulatory engagement on DRDL’s proposed activity, an initial intervention was held between DRDL and other relevant regulatory bodies that focussed on clarifying understanding of the activity being requested and structure and content of the supporting PSC [ref. [7]].

# Matters arising from ONR’s work

## ONR’s work

The matters arising from the work carried out by ONR are summarised as follows.

The fault studies inspector has reviewed DRDL’s PSC and undertaken a targeted assessment of DRDL’s control of criticality, as this was considered to be the primary risk associated with the requested activity. Specifically this focussed on any new or novel activities when compared to previous dockings.

In summary, the inspector advised that the:

Modification justified by the PSC has been categorised in accordance with regulatory expectations, specifically ONR technical inspection guide for LC 22 [ref. [8]].

Hazard identification has undergone a reasonable process of review and was complimented by new studies, as appropriate when compared to relevant good practice (RGP) of ONR Safety Assessment Principles (SAPs) FA.2 [ref. [8]].

Inclusion of severe accident analysis in the PSC now aligns to regulatory expectations when compared to the relevant ONR SAPs.

The improvements and forward actions identified by the PSC are risk informed, consistent with regulatory expectations when compared to RGP of ONR SAPs, including FA.6 and FA.7.

DNSR has, as the competent body, provided sufficient assurance against certain claims made by the PSC on the intrinsic withstand of the submarine when compared to ONR analysis validation (AV) range of SAPs and associated technical assessment guide.

The inspector did note some shortfalls against regulatory expectations. However, the inspector is satisfied that DRDL has both demonstrated that the risks are reduced to as low as reasonably practicable (ALARP) for the next docking, and recognised these shortfalls with forward commitments to manage the risk below the regulatory target limits identified in the ONR SAPs on a risk prioritised basis.

In conclusion, the inspector has not identified any safety issues that would prevent ONR agreeing to DRDL’s request and supports permission being granted [ref. [9]].

The C&I inspector has reviewed DRDL’s PSC and undertaken targeted assessment of the dockside cranes’ hoist rope payout protection system. This is because it has been modified including the addition of a computer-based protection channel which is unlike the extant crane protection systems that utilise hard-wired relay logic. This system protects against ledged loads which could result in dockside crane collapse.

In summary, the inspector acknowledges DRDL’s introduction of a second diverse channel to improve the engineered protection to reduce the possibility of a hazardous ledged load occurring. Noting that DRDL has placed conservatively reduced claims on the system pending future work to improve them based on operational and test data, the inspector advises that a suitable justification has been provided to demonstrate that the risks have been reduced to ALARP. In forming this view, the inspector judges that the risks have been reduced in accordance with regulatory expectations when compared to RGP of ONR SAPs ESS.27, ESS.21, EDR.1 and EDR.2 and associated technical assessment guides [ref. [8]].

The inspector did raise a query associated with configuration control if replacing the smart devices. Specifically this was related to unknown software modifications that could undermine the proven in use data underpinning the claimed reliability. At the time, the inspector was unable to source any documented evidence that formal arrangements exist to mitigate this risk. The inspector therefore raises a recommendation for DRDL to provide adequate arrangements for procuring smart devices including assurance that the device firmware version is aligned to the relevant safety system substantiation. The inspector does not consider this to be a prerequisite to granting permission and therefore it will be subject to regulatory monitoring via a formal regulatory issue [ref. [10]].

In conclusion, the inspector has not identified any safety issues that would prevent ONR agreeing to DRDL’s request and supports permission being granted [ref. [11]].

The human factors inspector has reviewed DRDL’s PSC and undertaken a targeted assessment of the potential risk significant faults that place the greatest reliance on human actions including both operator event initiators and safeguards to prevent, protect or mitigate the consequences of a fault. This focussed on whether the PSC provided evidence of the feasibility and reliability of claimed human actions.

In summary, the inspector advises that:

DRDL has undertaken a systematic approach to identify actions important to safety and the operating rules that ensure the safe operating envelope is maintained.

DRDL has adequately integrated human factors within the design and PSC.

Human factors involvement in the design has resulted in the application of general good practice design principles and improvements to useability. In forming this opinion, the inspector did require DRDL to provide additional validation and verification evidence of the design to support reliable operations and associated safety important tasks.

The inspector did identify some gaps from regulatory expectations when compared to RGP of ONR SAPs EHF.1-.10 and associated technical assessment guides [ref. [8]]. This included a minor shortfall in the effective interfacing between the human factors design and PSC work. However, following several engagements with DRDL, the inspector judges that these are evidential reporting gaps to the work undertaken by DRDL rather than gaps to nuclear safety. The inspector therefore advises that it would be disproportionate to withhold granting permission when no specific safety gaps have been identified. The inspector does however, raise a recommendation for DRDL to review the gaps to identify any associated improvements to DRDL’s arrangements/their implementation. The inspector does not consider this to be a prerequisite to granting permission and therefore it will be subject to regulatory monitoring via a formal regulatory issue [ref. [10]].

In conclusion, the inspector has not identified any safety issues that would prevent ONR agreeing to DRDL’s request and supports permission being granted [ref. [12]].

In addition, the human factors inspector also provided advice via an inspection of DRDL’s compliance with implementation of its LC 22 arrangements [ref. [13]] with a specific focus on LC 10: Training and LC 24: Operating Instructions for dockside  operations. These were targeted given that the PSC identifies administrative controls are required to keep the facility within its safe operating envelope during both normal operations and potential fault scenarios. The purpose of the inspection was to gain assurance of DRDL's ability to implement the PSC’s administrative requirements and readiness of the people and processes to commence the requested activity.

Based on the evidence sampled at the time of the inspection against DRDL’s arrangements and documentation, and regulatory guidance DRDL was judged to have adequately implemented its arrangements for compliance with LC 22: Modification or experiment on existing plant. Specifically that for the proposed modification DRDL has:

provided adequate documentation to justify the safety of it;

provided suitable training for those on site who have responsibility for any operations which may affect safety; and

operating instructions that include instructions in the interests of safety and instructions necessary to ensure operating rules are implemented.

In conclusion, it was judged that RGP was met when compared with appropriate benchmarks; legal duties were complied with; and, no safety shortfalls were identified in the delivery of safety functions.

Both the mechanical and civil engineering inspectors provided advice via inspections of DRDL’s compliance with implementation of its LC 28 arrangements for the facility’s mechanical and civil engineering SSCs respectively [refs. [14] & [15]]. The purpose of the inspections was to gain assurance of DRDL's ability to implement the PSC’s requirements for these SSCs and plant readiness to commence the requested activity.

Based on the evidence sampled at the time of the inspections against DRDL's arrangements and documentation, and regulatory guidance DRDL was judged to have implemented adequately its arrangements for compliance with LC 28: Examination, maintenance, inspection and testing. Specifically that it was carried out:

By suitably qualified and experienced persons;

In accordance with schemes laid down in writing;

Within the intervals specified in the plant maintenance schedule;

Under the control and supervision of a suitably qualified and experienced person appointed by the licensee for that purpose; and

With a signed and dated report of completed examination, maintenance, inspection and testing.

In conclusion, both inspectors advised that RGP was met when compared with appropriate benchmarks; legal duties were complied with; and, no safety shortfalls were identified in the delivery of safety functions.

## External governance and assurance

As part of my initial consideration of DRDL’s request, I confirmed that in accordance with its established governance and assurance arrangements, the PSC justifying DRDL’s request had been subject to independent consideration and advice from its Nuclear Safety Committee (NSC) [ref. [16]]. No formal advice was provided by the NSC to DRDL other than that it should endorse it.

The Environment Agency and DNSR regulatory bodies have both advised that they have no objection to ONR agreeing to DRDL’s request [refs. [17] & [18]].

# Conclusions

Based on the work carried out by ONR, I judge that for the requested agreement, DRDL has provided adequate documentation to justify the safety of the proposed modification and demonstrated that there will be suitable and sufficient safety measures in place to ensure that the risks from normal activities and reasonably foreseeable faults will be ALARP. We have not identified any safety shortfalls that would prevent agreement to DRDL’s request and as such, I consider that DRDL has adequately implemented its arrangements made under LC 22(1).

# Recommendations

In accordance with the provisions made in DRDL’s arrangements under LC 22(1), ONR should issue Licence Instrument 569 [ref. [19]] agreeing to DRDL’s request [ref. [1]].

ONR should also maintain regulatory oversight and routinely monitor progress against the identified assessment recommendations via formal regulatory issues to ensure that they are adequately addressed by DRDL within the required timescales.

# References

| [1] | DRDL, Ref. FE-201096 (SG-bs) - Request for agreement to undertake the docking and associated base maintenance period upkeep of Astute Class Submarines in 15 Dock. ONR Ref. ONRW-2019369590-8597. |
| --- | --- |
| [2] | ONR, Licence Condition Handbook. https://www.onr.org.uk/publications/regulatory-guidance/other-guidance/. |
| [3] | DRDL, Ref. PSC250A - 15 Dock Plant Safety Case for Astute BMP. March 2024. Copy not held by ONR. |
| [4] | ONR Business Management System - Guidance. https://www.onr.org.uk/. |
| [5] | ONR, Ref. PR-01076 - Internal Permissioning Record for 15 Dock ABMP. |
| [6] | ONR, Agreements with others. https://www.onr.org.uk/working-with-others/agreements-with-others/. |
| [7] | ONR, Devonport Royal Dockyard Ltd (DRDL) 15 Dock PSC Overview - Ref. ONR-OFD-CR-23-654. 21 February 2024. |
| [8] | ONR, Regulatory Guidance, https://www.onr.org.uk/publications/regulatory-guidance/. |
| [9] | ONR, Fault Studies Assessment of the Astute Base Maintenance Period (ABMP) LC 22 Submission, Issue 1, September 2024, ONR Ref. ONRW-2126615823-4410. |
| [10] | ONR, Management of Regulatory Issues, ONR-RIO-PROC-001, https://www.onr.org.uk/publications/regulatory-guidance/. |
| [11] | ONR, AR-01560 Control and Instrumentation Assessment of 15 Dock Astute Class Base Maintenance Period PSC 250A, Issue 1, September 2024, ONR Ref. ONRW-2126615823-4217. |
| [12] | ONR, Human Factors Assessment of 15 Dock Astutue Class Base Maintenance Period (PSC 250A), Issue 1, August 2024, ONR Ref. ONRW-2126615823-3921. |
| [13] | ONR, Ref. IIS-51055 - Human Factors LC 22 Inspection Record. 7 January 2025, https://www.onr.org.uk/publications/regulatory-reports/site-specific-reports/. |
| [14] | ONR, Ref. IR-52842 - Mechanical Engineering LC 28 Inspection Record. 10 January 2024, https://www.onr.org.uk/publications/regulatory-reports/site-specific-reports/. |
| [15] | ONR, Ref. IR-52839 - Civil Engineering LC 28 Inspection Record. 6 February 2024, https://www.onr.org.uk/publications/regulatory-reports/site-specific-reports/. |
| [16] | DRDL, Ref. NSC/266 - Minutes of Meeting Nuclear Safety Committee 266. 12 March 2024. ONR Ref. ONRW-2019369590-9058. |
| [17] | Environment Agency advice on DRDL Docking Activities. E-mail dated 22 July 2024. ONR Ref. ONRW-2019369590-11228. |
| [18] | DNSR’s advice on DRDL’s request to commence ABMP. DNSR. E-mail dated 16 September 2024. ONR Ref. ONRW-2019369590-12966. |
| [19] | ONR, Licence Instrument No. 569, Ref. DRDL71422N. ONR Ref. ONRW-2019369590-13073. |